RFP Form for egeplast SLM® Sewage Pressure Pipe

Preliminary note:

Sewage pressure pipe in accordance with DIN 8074/8075, DIN EN 12201, made of PE 100-RC acc. to PAS 1075, with the highest resistance to slow crack growth; pipe colour black; verified in accordance with DIN 8075 as well as DIN Certco in acc. with ZP 14.3.1, labelled with the DIN Certco DINplus mark of conformity, with a continuously extruded protective coating made of polyolefin (brown akin to RAL 8023), with yellow-green stripes akin to RAL 6018.

Piping construction according to PAS 1075 Type 3, pipe with dimensions according to DIN 8074 with an external protective layer.

Butt fusion jointing without removal of the protective coating, welding according to the relevant guidelines. Suitability for butt fusion jointing without cutback (removal of the protective coating) hast to be confirmed by an independent testing institute.

The monitoring and certification of constant material quality as well as the regular component testing acc. to PAS 1075 is carried out by an independent testing and inspection institute which is accredited by the “Deutsches Institut für Bautechnik” DIBT (German approval body for construction products an types of construction), Berlin .

Pipe manufacturer certified acc. to DIN EN ISO 9001 (quality management), DIN EN ISO 14001 (environmental management) as well as DIN EN ISO 50001 (energy management).

All necessary butt fusion joints are to be made according to the requirements of the relevant technical guidelines, corresponding welding parameters for polyethylene apply. The joints are to be performed according to the pipe manufacturer’s current technical manual.

Product:	egeplast SLM® sewage pressure pipe

made of PE 100-RC or equivalent

Manufacturer:	egeplast international GmbH

Robert-Bosch-Str. 7

D-48268 Greven, Germany

Tel.: +49.2575.9710-0

Fax: +49.2575.9710-110

e-mail: info@egeplast.de

http://www.egeplast.de 		http://www.egeplast.eu

Specification of services:	egeplast SLM® sewage pressure pipe made of PE 100-RC with dimensions:

________mm, SDR _____

delivered as straight lengths of 6 / 12 m

delivered as bundled coils in lengths_____ of m

Deliver_______ running metres and install professionally according to DIN and appropriate installation guidelines:______________ € / running metre